## Instructions
TESTING LEAD CONTENT IN DRINKING WATER OF SCHOOL FACILITIES
2021/22 Reports - Instructions
INTRODUCTION |  | If this workbook opens in Excel Online, click the ellipses and then click download
This guide has been written to assist school districts with the submission of their reports on testing lead content in drinking water of school facilities.
The following tabs are provided for your reference and use: 1. Instructions: Guide for completing the report for testing lead content in drinking water of school facilities 2. Lead Content Testing Report: Worksheet to capture water quality report and data for tested or assessed facilities.
NOTE - School districts must complete lead content testing on all school facilities once every 3 years. Therefore a minimum of 1/3 (or 33%) of the school facilities in a school district’s inventory must be tested each year. The Ministry of Education expects that all facilities in VFA Facility be tested. Please contact Nathan Whipp if you need assistance accessing VFA Facility.
All fields are to be completed except those that are greyed out.
The completed spreadsheet must be emailed by March 31, 2022 attention Nathan Whipp, Program Evaluation Analyst, at:
CapitalManagementBranch@gov.bc.ca
School districts are responsible for verifying all information provided to the Ministry of Education
SUBMISSION HEADINGS | INSTRUCTION
SCHOOL DISTRICT INFORMATION
SD No. | Enter the school district number.
SD Name | The school district name will populate automatically when the SD No. is entered.
SD Contact Name | Provide the name of the primary school district contact regarding report submission.
SD Contact Phone | Provide the phone numbers of school district's contact person.
Report Date | Indicate the date of when the report is submitted to The Ministry of Education
HEALTH AUTHORITY (HA) INFORMATION
Region | Provide the name of health authority region where your school district is located.
Contact Name | Provide contact name of health authority officer/staff that worked with your district in completing this report.
Contact Phone | Provide contact phone numbers of health authority officer/staff that worked with your district in completing this report.
Report Submitted to HA | Did your school district submitt this report to the Health Authority? (YES/NO).
Report Submission Date | Indicate the date of when the report was submitted to the Health Authority (e.g., January 10, 2022).
SCHOOL FACILITY INFORMATION
SD Number | Value will populate automatically as per entry above.
Ministry Facility Code | The Ministry Facility Code as per the School Master List - http://www.bced.gov.bc.ca/apps/imcl/imclWeb/SchoolContactSelector.do If the code or name is incorrect, please follow the update instructions as per the site.
School Facility Name | Indicate the name of the facility, including school type (i.e. Elementary, Middle, or Secondary), for additional structure. If the facility is not in VFA please provide the address of the facility within the School Facility Name. Please do not enter program names, instead enter the Facility Name and if desired the program name in brackets.
Year Built | Indicate the year of when the school facility was built.
Date of Test (mm/yyyy) | Indicate the date of when the facility was tested (e.g., Jun-21 for June 2021).
Total Samples | Indicate the total samples taken for testing. For example, input two (2) if pre- and post-flush water samples were taken.
Water Fixture Type | Select the type of water fixture tested from the dropdown menu: Sink, Tap, Water Fountain, Water Filling Station, Pipe, and Other.
Room Location | Indicate the room/area location where the test was sampled.
Lead Level Result (mg/L) | Provide Lead Level Result (in mg/L) for each sample taken. Apply appropriate conversion if sample was measured in unit other than mg/L (milligrams per liter).
Exceed Maximum Acceptable Concentrations | The pass or fail indication (No or Yes) will populate automatically after test result is provided. If sample results reveal lead levels above the maximum allowable concentration of 0.005 mg/L as stated from the Guidelines for Canadian Drinking Water Quality by Health Canada, the school district in consultation with their Regional Health Authority must commence daily flushing immediately, or deactivate and place a “Not in Use” sign on the water source.
MITIGATION STRATEGY & PUBLIC COMMUNICATION PLAN
Mitigation Strategy Description | Describe mitigation strategy for schools that show lead levels above the maximum allowable concentration of 0.005 mg/L as stated from the Guidelines for Canadian Drinking Water Quality by Health Canada.
Describe Public Communication Plan | Describe public communication plan should testing result in elevated levels of lead.
ADDITIONAL INFORMATION
Comments | Provide additional comments, as may be required.
Next scheduled date of testing (mm/yyyy) | Provide the date of when the facility is scheduled for another water quality testing. School districts must complete lead content testing on all school facilities once every 3 years. Therefore a minimum of 1/3 (or 33%) of the school facilities in a school district’s inventory must be tested each year.
Ministry Submission Period | This field will be used by the Ministry of Education for data inventory purposes.

## Lead Content Testing Report
Ministry of Education - Capital Management Branch
2021/22 REPORT FOR TESTING LEAD CONTENT IN DRINKING WATER OF SCHOOL FACILITIES
School District Information |  | Health Authority (HA) Information
SD No. | 8 | Region | Interior Health
SD Name | Kootenay Lake | Contact Name | Gordon Moseley
SD Contact Name: | Russell Warwick | Contact Phone | 250-549-5725
SD Contact Phone: | 250-505-8242 | Report Submitted to HA | Yes
Report Date | 2021-03-25 | Report Submission Date | 2020-02-25
Click here to access the School Master List for Facility Names and Facility Codes
SCHOOL FACILITY INFORMATION |  |  |  | TEST INFORMATION | [5 empty] | MITIGATION STRATEGY & PUBLIC COMMUNICATION PLAN |  | ADDITIONAL INFORMATION
School District Number | Ministry Facility Code | School Facility Name | Year Built | Date of Test (mm/yyyy) | Total Samples | Water Fixture Type | Room Location | Lead Level Result (mg/L) | Exceed Maximum Acceptable Concentrations | Mitigation Strategy Description | Describe Public Communication Plan | Comments | Next Scheduled Date of Testing (mm/yyyy) | Ministry Submission Period
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Library | 29 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 1 | 0.883 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Library | 0.173 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Library | 0.103 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 3 | 0.0963 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 1 | 0.0632 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 1 | 0.0602 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Library | 0.0565 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Gym Kitchen | 0.0449 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2020-02-20 | 2 | Sink | Kidz Klub | 0.0356 | Yes | Sink is currently being flushed. Signage Posted to Not Use. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2023-02-23 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2020-02-20 | 2 | Water Fountain | In Music Room | 0.0313 | Yes | Disabled. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 1st Floor Hallway Outside Art Room (Room 115) | 0.0253 | Yes | Disabled Pending Replacement with Water Fill Station w/ Filter | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 1 | 0.031 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2021-05-18 | 2 | Sink | Staffroom | 0.0166 | Yes | Fixture Replaced and Water Resampled. Water still high but lower than previous .108 mg/L. Daily Flush required. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Sink | Canteen | 0.0127 | Yes | Flush until Fixture is Changed and Resampled | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Gym Kitchen | 0.0146 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2021-05-20 | 2 | Sink | Classroom | 0.0119 | Yes | Replaced Fixture and Re-tested. Fixture still High. Signage to not drink posted. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Sink | Foods Room | 0.0116 | Yes | Fixture has been replaced. Continuing flushing until resampling performed. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 899225 | REACH |  | 2020-02-20 | 2 | Sink | Industrial Kitchen - Basin Sink (1st Floor) | 0.011 | Yes | Location to be Flushed. Fixture Replacement Planned. | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807026 | W.E. Graham Community School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.0104 | Yes | Non-Potable Signage In Place. School has known issue and is provided bottled water/filtered water from water filling station | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | Girls Change room on 3rd Floor | 0.0098 | Yes | Faucet Disabled in 2021, Pending Removal | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 |  | Creston Bus Garage |  | 2019-12-01 | 2 | Sink | Staffroom on 2nd Floor | 0.00859 | Yes | Informed the site, Site has bottled water. | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Gym Kitchen | 0.00972 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Staff Room | 0.00934 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Staff Room | 0.00875 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 3 | 0.00867 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 899178 | Wildflower |  | 2019-12-01 | 2 | Sink | Staffroom on 2nd Floor (Wildflower) | 0.00854 | Yes | Staffroom to be relocated in 2022 and Fixture removed. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2020-02-20 | 2 | Sink | Kidz Klub | 0.00828 | Yes | Sink is currently being flushed. Signage Posted to Not Use. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2023-02-23 | 2022-03-30
8 | 899225 | REACH |  | 2021-05-03 | 2 | Sink | Backroom of Reach (1st Floor) | 0.00797 | Yes | Fixture removal planned | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2021-05-20 | 2 | Sink | Staffroom | 0.00785 | Yes | Replaced Fixture and Re-tested. Fixture still High. Daily Flush Implemented | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Staff Room | 0.00797 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 106 | 0.00537 | Yes | Disabled. Planned Drinking Water Bottle Fill Station or Permanent Removal | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 3 | 0.00704 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Fountain | Location 3 | 0.00579 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 886019 | Erickson Elementary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00493 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Gym Kitchen | 0.00505 | Yes | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Sink | Foods Room | 0.00461 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside 1st floor Boys Washroom | 0.0043 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Downstairs Hallway outside Wildflower Classrooms | 0.00414 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2020-02-20 | 2 | Sink | Kitchen off the Gym | 0.00385 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886005 | Jewett Elementary |  | 2021-05-19 | 2 | Sink | Staffroom | 0.00378 | No | Changed Fixtures, Retested in May | Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2023-02-01 | 2022-03-30
8 |  | Nelson Bus Garage |  | 2019-12-01 | 2 | Sink | Kitchen | 0.00365 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 9393003 | SD93 Ecole des Sentiers-alpins |  | 2021-05-02 | 2 | Sink | Staffroom | 0.00364 | No | Replaced Fixture and Re-tested | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00353 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Filling Station | Location 2 | 0.00357 | No | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Water Fountain | Down the Hallway off of the Gym | 0.00353 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00332 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2021-05-18 | 2 | Sink | Outside Room 108 | 0.00326 | No | Fixture Replaced and Water Resampled. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside Room 303 | 0.00317 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00296 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00289 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside 2nd floor Boys Washroom | 0.00277 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00272 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Sink | Canteen | 0.00262 | No | Flush until Fixture is Changed and Resampled | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Sink | Staff Room | 0.00267 | No | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 1st Floor Hallway Outside Art Room (Room 115) | 0.00262 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807035 | Redfish Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway, Outside of Boys Washroom | 0.00249 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Upstairs Hallway Outside Room 230 | 0.0023 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 302 | 0.00228 | No | Disabled. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2020-02-20 | 2 | Water Fountain | In Music Room | 0.00228 | No | Disabled. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807035 | Redfish Elementary School |  | 2021-05-19 | 2 | Sink | Staffroom | 0.00212 | No | Replaced Fixture and Re-tested | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Sink | Staffroom on 2nd Floor | 0.00204 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Sink | Foods Room | 0.00196 | No | Flush until Fixture is Changed and Resampled | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | Girls Change room on 3rd Floor | 0.00192 | No | Faucet Disabled in 2021, Pending Removal | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807026 | W.E. Graham Community School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00187 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2021-05-20 | 2 | Sink | Classroom | 0.00179 | No | Replaced Fixture and Re-tested. Fixture still High. Signage to not drink posted. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Filling Station | Location 2 | 0.00182 | No | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside the Shop | 0.00177 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Inside Boys Change room off the Gym | 0.00174 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 2nd Floor Hallway outside Staffroom | 0.00152 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2019-12-01 | 2 | Sink | Room 307 (Staffroom) | 0.0015 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2021-05-01 | 2 | Sink | Foods Room | 0.0015 | No | Changed Fixtures, Retested in May | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 302 | 0.00149 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Filling Station | Location 2 | 0.00147 | No | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 110 | 0.00144 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807035 | Redfish Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway, Outside of Boys Washroom | 0.00141 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Sink | Downstairs Room Next to Music Room | 0.00132 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2021-05-20 | 2 | Sink | Staffroom | 0.00131 | No | Replaced Fixture and Re-tested. Fixture still High. Daily Flush Implemented | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside Room 171 | 0.00127 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 9393007 | SD93 Ecole des Sentiers-alpins |  | 2019-12-01 | 2 | Water Fountain | Outside Salle 6 | 0.00126 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 00807016 | Blewett Elementary School |  | 2019-06-01 | 4 | Water Filling Station | Location 2 | 0.00126 | No | Site is currently on a Do No Drink order from Interior Health Authority and is being provided with bottled water. | Site to send out communication to parents | Water from the site is currently on a Do Not Drink order and bottled water is provided. Testing was performed by a consultant 4 months after water system was put on the order. | Prior to system startup | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Outside of Room 202/204 | 0.00122 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | Commerce Block, Outside Washroom | 0.00114 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2019-12-01 | 2 | Water Fountain | Hallway outside 3rd floor Staffroom (Room 307) | 0.00113 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00109 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside Room 303 | 0.00108 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 899178 | Wildflower |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Hallway, outside the Staffroom (Wildflower) | 0.00106 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Sink | Maintenance Building | 0.00105 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2023-02-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Water Fountain | Outside Room C112/C113 | 0.00104 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2023-02-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 124A | 0.00102 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 2nd Floor Hallway behind Gym/Theatre (Room 226) | 0.00102 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00101 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 2nd Floor Hallway outside Staffroom | 0.001 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Water Fountain | 1st Floor Hallway, Outside Room 102 | 0.00098 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym (Lower Fountain) | 0.00093 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 104 | 0.00092 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807012 | Salmo Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00092 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 113/116 | 0.0009 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 3rd Floor Hallway Outside Girls Washroom | 0.00087 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Sink | 2nd Floor Staffroom | 0.00086 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807030 | Gordon Sargent |  | 2019-12-01 | 2 | Sink | Near Bathrooms | 0.00084 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807032 | Gordon Sargent |  | 2019-12-01 | 2 | Sink | South End of Building | 0.00084 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00082 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym (Higher Fountain) | 0.00082 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 113/116 | 0.00082 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Water Fountain | In Hallway of Old Annex | 0.00082 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Downstairs Hallway outside Wildflower Classrooms | 0.00081 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2020-02-20 | 2 | Sink | Kitchen off the Gym | 0.00078 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside Room 171 | 0.00078 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 3rd Floor Hallway Outside Boys Washroom | 0.00074 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Upstairs Hallway Outside Room 230 | 0.00074 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside 2nd floor Girls Washroom | 0.0007 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 9393005 | SD93 Ecole des Sentiers-alpins |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym | 0.0007 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Sink | Staffroom on 2nd Floor | 0.00069 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Sink | Foods Room | 0.00066 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym (Lower Fountain) | 0.00065 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym (Higher Fountain) | 0.00062 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Sink | Staffroom | 0.00062 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2023-02-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 3rd Floor Hallway Outside Boys Washroom | 0.00061 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2019-12-01 | 2 | Water Filling Station | Hallway outside Room 115 | 0.0006 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886006 | Crawford Bay Elem-Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside the Shop | 0.0006 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Inside Girls Change room off the Gym | 0.0006 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Hallway, Outside Staff Room | 0.00059 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside 1st floor Boys Washroom | 0.00059 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00059 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Water Filling Station | 3rd Floor Hallway, Outside Room 302 | 0.00057 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 899178 | Wildflower |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Hallway, outside the Staffroom (Wildflower) | 0.00057 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 110 | 0.00056 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807028 | Gordon Sargent |  | 2019-12-01 | 2 | Sink | Kitchen | 0.00055 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 2nd Floor Hallway Outside Gym | 0.00054 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00053 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 2nd Floor Hallway behind Gym/Theatre (Room 226) | 0.00052 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 9393009 | SD93 Ecole des Sentiers-alpins |  | 2019-12-01 | 2 | Water Fountain | Outside Salle 4 | 0.00052 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 899178 | Wildflower |  | 2020-02-20 | 2 | Water Fountain | Outside Gym | 0.0005 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | Commerce Block, Outside Washroom | 0.00048 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2019-12-01 | 2 | Water Filling Station | Hallway outside Room 115 | 0.00048 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym | 0.00048 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Water Fountain | Down the Hallway off of the Gym | 0.00044 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 899178 | Wildflower |  | 2019-12-01 | 2 | Sink | Staffroom on 2nd Floor (Wildflower) | 0.00042 | No | Staffroom to be relocated in 2022 and Fixture removed. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside Room 108A | 0.0004 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside 2nd floor Boys Washroom | 0.0004 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886019 | Erickson Elementary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00039 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807018 | Rosemont Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 106 | 0.00038 | No | Disabled. Planned Drinking Water Bottle Fill Station or Permanent Removal | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Water Filling Station | 3rd Floor Hallway, Outside Room 302 | 0.00035 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 899225 | REACH |  | 2020-02-20 | 2 | Sink | Industrial Kitchen (1st Floor) | 0.00035 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Hallway, Outside Staff Room | 0.00033 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside 2nd floor Girls Washroom | 0.00033 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 |  | Creston Bus Garage |  | 2019-12-01 | 2 | Sink | Staffroom on 2nd Floor | 0.00033 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside the Office | 0.00032 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807026 | W.E. Graham Community School |  | 2019-12-01 | 2 | Water Filling Station | Hallway outside of the Custodian Closet | 0.00031 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 9393004 | SD93 Ecole des Sentiers-alpins |  | 2021-05-02 | 2 | Sink | Staffroom | 0.00031 | No | Replaced Fixture and Re-tested | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 9393006 | SD93 Ecole des Sentiers-alpins |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym | 0.00031 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 9393008 | SD93 Ecole des Sentiers-alpins |  | 2019-12-01 | 2 | Water Fountain | Outside Salle 6 | 0.00031 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 9393010 | SD93 Ecole des Sentiers-alpins |  | 2019-12-01 | 2 | Water Fountain | Outside Salle 4 | 0.00031 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2021-05-01 | 2 | Sink | Foods Room | 0.0003 | No | Changed Fixtures, Retested in May | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2021-05-18 | 2 | Sink | Outside Room 108 | 0.00029 | No | Fixture Replaced and Water Resampled. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Inside Girls Change room off the Gym | 0.00029 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside the Office | 0.00028 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Water Fountain | Outside Room 108A | 0.00026 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807026 | W.E. Graham Community School |  | 2019-12-01 | 2 | Water Filling Station | Hallway outside of the Custodian Closet | 0.00026 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2021-05-18 | 2 | Sink | Staffroom | 0.00026 | No | Fixture Replaced and Water Resampled. Water still high but lower than previous .108 mg/L. Daily Flush required. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807035 | Redfish Elementary School |  | 2021-05-19 | 2 | Sink | Staffroom | 0.00024 | No | Replaced Fixture and Re-tested | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886019 | Erickson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside Classroom 02 | 0.00024 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Inside Boys Change room off the Gym | 0.00023 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Water Fountain | Outside Gym Change Rooms | 0.00022 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00022 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2021-04-30 | 2 | Water Fountain | Hallway outside 2nd Floor Office | 0.00022 | No | Replaced with Bottle Fill Station, Retested in April 2021 | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Outside of Room 202/204 | 0.00021 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Water Fountain | Outside Gym Change Rooms | 0.00021 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00021 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.00021 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886019 | Erickson Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside Classroom 02 | 0.00021 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 899178 | Wildflower |  | 2020-02-20 | 2 | Water Fountain | Outside Gym | 0.00021 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 899225 | REACH |  | 2021-05-03 | 2 | Sink | Backroom of Reach (1st Floor) | 0.00021 | No | Fixture removal planned | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Water Fountain | Outside Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807004 | Hume Elementary School |  | 2019-12-01 | 2 | Water Fountain | Outside Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807005 | Trafalgar Middle School |  | 2019-12-01 | 2 | Sink | Staffroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2021-05-01 | 2 | Water Fountain | Hallway outside Room 110 | 0.0002 | No | Replaced with Bottle Fill Station, Retested in May | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2021-05-01 | 2 | Water Fountain | Hallway outside Room 110 | 0.0002 | No | Replaced with Bottle Fill Station, Retested in May | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 104 | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807011 | Salmo Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside Room 124A | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807012 | Salmo Secondary |  | 2019-12-01 | 2 | Water Filling Station | Outside the Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807012 | Salmo Secondary |  | 2019-12-01 | 2 | Water Filling Station | Outside the Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807012 | Salmo Secondary |  | 2019-12-01 | 2 | Sink | Staffroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 1st Floor Hallway Outside Boys Washroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 1st Floor Hallway Outside Boys Washroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Hallway On the Far Wall outside the Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Filling Station | 2nd Floor Hallway On the Far Wall outside the Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 2nd Floor Hallway Outside Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807013 | L V Rogers Secondary |  | 2019-12-01 | 2 | Water Fountain | 3rd Floor Hallway Outside Girls Washroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2021-04-30 | 2 | Water Fountain | Hallway outside 2nd Floor Office | 0.0002 | No | Replaced with Bottle Fill Station, Retested in April 2021 | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2019-12-01 | 2 | Water Fountain | Hallway outside 3rd floor Staffroom (Room 307) | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2020-02-20 | 2 | Sink | Outside the Staffroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2020-02-20 | 2 | Sink | Outside the Staffroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807014 | South Nelson Elementary |  | 2019-12-01 | 2 | Sink | Room 307 (Staffroom) | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Water Filling Station | Outside Gym Rear | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 807025 | Mount Sentinel Secondary |  | 2019-12-01 | 2 | Water Filling Station | Outside Gym Rear | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 807029 | Gordon Sargent |  | 2019-12-01 | 2 | Sink | Kitchen | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807031 | Gordon Sargent |  | 2019-12-01 | 2 | Sink | Near Bathrooms | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807033 | Gordon Sargent |  | 2019-12-01 | 2 | Sink | South End of Building | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside the Gym | 0.0002 | No | Replaced with Bottle Fill Station. Resampled in May 2021. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 807034 | Winlaw Elementary School |  | 2019-12-01 | 2 | Water Fountain | Hallway outside the Gym | 0.0002 | No | Replaced with Bottle Fill Station. Resampled in May 2021. | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Sink | 2nd Floor Staffroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Sink | Downstairs Room Next to Music Room | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Filling Station | Outside 1st Floor Girls Washroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886004 | Adam Robertson Elementary |  | 2019-12-01 | 2 | Water Filling Station | Outside 1st Floor Girls Washroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886005 | Jewett Elementary |  | 2021-05-19 | 2 | Water Fountain | Outside Girls Washroom/Across from the Furnace Room | 0.0002 | No | Replaced with Bottle Fill Station, Retested in May | Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2023-02-01 | 2022-03-30
8 | 886005 | Jewett Elementary |  | 2021-05-19 | 2 | Water Fountain | Outside Girls Washroom/Across from the Furnace Room | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2023-02-01 | 2022-03-30
8 | 886005 | Jewett Elementary |  | 2021-05-19 | 2 | Sink | Staffroom | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2023-02-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Cafeteria | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Cafeteria | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Hallway outside the Staffroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Fountain | Hallway outside the Staffroom | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Filling Station | Mezzanine | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886007 | Kootenay River Secondary |  | 2019-12-01 | 2 | Water Filling Station | Mezzanine | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Water Fountain | In Hallway of Old Annex | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886014 | Canyon/Lister Elementary |  | 2019-12-01 | 2 | Water Fountain | Outside the Gym | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Sink | Maintenance Building | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2023-02-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Water Fountain | Outside Room C112/C113 | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2023-02-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Water Filling Station | Outside Staffroom/Office | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2023-02-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Water Filling Station | Outside Staffroom/Office | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2023-02-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Water Filling Station | Outside the Gym | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2023-02-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Water Filling Station | Outside the Gym | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2023-02-01 | 2022-03-30
8 | 886018 | J V Humphries Elem-Secondary |  | 2020-02-20 | 2 | Sink | Staffroom | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2023-02-01 | 2022-03-30
8 | 886019 | Erickson Elementary |  | 2019-12-01 | 2 | Water Filling Station | Outside Washrooms | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | First Draw | 2022-12-01 | 2022-03-30
8 | 886019 | Erickson Elementary |  | 2019-12-01 | 2 | Water Filling Station | Outside Washrooms | 0.0002 | No |  | News Release Issued for Entire District's results. Reports for each school generated and distributed to the principals to share with any interested party. | 5 Minute Flush | 2022-12-01 | 2022-03-30
8 | 899225 | REACH |  | 2020-02-20 | 2 | Sink | Industrial Kitchen - Basin Sink (1st Floor) | 0.0002 | No | Location to be Flushed. Fixture Replacement Planned. | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | 899225 | REACH |  | 2020-02-20 | 2 | Sink | Industrial Kitchen (1st Floor) | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 |  | Nelson Bus Garage |  | 2019-12-01 | 2 | Sink | Kitchen | 0.0002 | No |  | Reports for each school generated and distributed to the principals to share with any interested party. |  | 2022-12-01 | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30
8 | [8 empty] | - |  |  |  |  | 2022-03-30

## LOVs (hidden)
School Districts
SD# | School District
5 | Southeast Kootenay
6 | Rocky Mountain
8 | Kootenay Lake
10 | Arrow Lakes
19 | Revelstoke
20 | Kootenay-Columbia
22 | Vernon
23 | Central Okanagan
27 | Cariboo-Chilcotin
28 | Quesnel
33 | Chilliwack
34 | Abbotsford
35 | Langley
36 | Surrey
37 | Delta
38 | Richmond
39 | Vancouver
40 | New Westminster
41 | Burnaby
42 | Maple Ridge - Pitt Meadows
43 | Coquitlam
44 | North Vancouver
45 | West Vancouver
46 | Sunshine Coast
47 | Powell River
48 | Sea to Sky
49 | Central Coast
50 | Haida Gwaii
51 | Boundary
52 | Prince Rupert
53 | Okanagan Similkameen
54 | Bulkley Valley
57 | Prince George
58 | Nicola-Similkameen
59 | Peace River South
60 | Peace River North
61 | Greater Victoria
62 | Sooke
63 | Saanich
64 | Gulf Islands
67 | Okanagan Skaha
68 | Nanaimo-Ladysmith
69 | Qualicum
70 | Pacific Rim
71 | Comox Valley
72 | Campbell River
73 | Kamloops/Thompson
74 | Gold Trail
75 | Mission
78 | Fraser-Cascade
79 | Cowichan Valley
81 | Fort Nelson
82 | Coast Mountains
83 | North Okanagan-Shuswap
84 | Vancouver Island West
85 | Vancouver Island North
87 | Stikine
91 | Nechako Lakes
92 | Nisga'a
93 | Conseil Scolaire Francophone